Generic Specification For 

Accumulated Energy and Demand  Monitor

DMWH 300

2.    
PRODUCT

2.1  
POWER METERS

A.
The Monitor shall be UL listed and CE marked.

B.
The Monitor shall accept input from standard instrument transformers (5A secondary current transformers and 120 volt secondary potential transformers). The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.

1. The Monitor shall withstand 200% rated current continuously. It shall withstand 10X rated current for at least 3 seconds.

2. The Monitor shall be capable of connection to a three phase, four wire wye system or a three phase, three wire, open delta system.

3. Surge withstand shall conform to IEEE C37.90.1

4. The Monitor shall be user programmable to any PT or CT ratio.  DIP switches or other fixed ratio designs shall not be acceptable. 

5. Voltage and current connections shall be segregated from each other on the back of the monitor to provide safe connections.

6. The monitor shall store all data in a non-volatile Eeprom. No battery is needed to store data in event of power down.

C.
The Monitor shall have an accuracy of +/- 0.4% or better for wattage.

1. The Monitor must measure true RMS watts, watt-hours, and watt demand, and shall have separate positive and negative watt-hour accumulators 

D.
The Monitor must use 0.56” L.E.D. displays.  There must be one line of display that can optionally show watts, watt-hours, and watt demand. Watt/hr resolution shall be to 6 ½ digits. No multiplier factors are needed.

E.
The monitor shall include output options for analog milli-amp signals.

1. The Monitor shall have two channels of analog output, 0-1mA or 4-20mA, for positive and negative watt/hour readings.

F.
The monitor shall include output options for pulse outputs and relay/alarm outputs.

1. The Monitor shall have two form C, dry contact relay outputs for alarm or control and 1 KYZ pulse output related to Watts/HR.


2. The Monitor must be capable of tripping its dry contact outputs for over/under Wattage, both positive and negative

G.
The Monitor shall have the capability of utilizing either an RS232 or RS485 port for digital communications using an open ASCII-based protocol.

1. The Monitor shall have the capability of having up to 9999 separate addresses for multi-point communication.

2. The digital port connections shall be separated from the voltage and current connections.

H.
The monitor case shall be fully enclosed and shielded.

1. The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable. 

2. The Monitor shall have a separable input module that can be remote mounted up to 3 feet from the display mounting.

3. The Monitor shall be rated for use at temperature from –20oC to +70oC.

4. The Monitor shall have an optional enclosure for surface mounting

I.
The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC.

J.
The Monitor shall have a standard 4-year warranty.

K.
Acceptable product is Electro Industries / Gaugetech, Model DMWH300.  

1. Add the following suffixes for added options:




a.
(-NL) – 2 Dry Contact Relays and 1 KYZ Pulse Output


b.
(-G) - Direct voltage monitoring to 600 volts phase to phase

 


c.
(-K110) - Remote Mounting Kit




d.
(-B) – Surface Mount Fiberglass Enclosure


e.
(SDFI-1) – 0-1 mA analog retransmitter (2 channels)




f.
(SDFI-20) – 4-20 mA analog retransmitter (2 channels)


g.
(SF232DB2) - Digital RS232 port




h.
(SF485DB3) - Digital RS485 port

2. For specification information, contact:

Electro Industries/Gaugetech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741

Page 1 of 2                                                                         050505                                                        E104754b


