Generic Specification For

Three Phase Triple Display Voltage Monitor

## 3DVA120

2.    	PRODUCT

2.1  	POWER METERS

A.	The Monitor shall be UL listed and CE marked.

B.	The Monitor shall accept input from standard instrument transformers (120 volt secondary potential transformers). The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.

- The Monitor shall be capable of connection to a three phase, four wire wye system or a three phase, three wire, open delta system.

- Surge withstand shall conform to IEEE C37.90.1

- The Monitor shall be user programmable to any PT ratio. DIP switches or other fixed ratio designs shall not be acceptable.

- Voltage connections shall be segregated from all other connections on the back of the monitor to provide safe connections.

C.	The Monitor shall have an accuracy of +/- 0.25% or better for volts.

- The Monitor shall measure True RMS voltage, both phase to neutral and phase to phase.

- The Monitor must be capable of providing readings for both instantaneous and average readings.

- The Monitor shall monitor max/min average values for all voltage readings.

D.	The monitor shall include a three line, integrated, light-emitting diode (LED) display.

- The measured values must be displayed on LED’s that are at least 0.56” high on each of the 3 separate lines.

- Each phase of voltage shall be displayed on a separate line simultaneously.   .

- The display must provide user access to max/min values for all displayed quantities.

- The user must have the capability to toggle between phase to neutral and phase to phase voltages.

E.	The monitor shall include output options for analog milli-amp signals.

- The Monitor shall have up to 4 channels of analog output, 0-1mA or 4-20mA.

- The analog outputs must map to any of the instantaneous readings.

- The analog output connections shall be separated from the voltage connections.

F.	The Monitor shall have two form C, dry contact relay outputs for alarm or control.

- The Monitor must be capable of tripping its dry contact outputs for over/under voltage, both on phase to phase and phase to neutral for all phases, for voltage imbalance, and for overage on %THD/Kfactor.

G.	The Monitor shall have the capability of utilizing either an RS232 or RS485 port for digital communications using an open ASCII-based protocol.

- The Monitor shall have the capability of having up to 9999 separate addresses for multi-point communication.

- The digital port connections shall be separated from the voltage connections.

H.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable.

- The Monitor shall have a separable input module which can be remote mounted up to 3 feet from the display mounting.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

I.	The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC.

J.	The monitor shall be capable of gathering and reporting harmonic data.

- The Monitor shall calculate the harmonic signature, %THD and K-Factor for all voltage inputs with valid data for harmonic spectrum capability to the 31st harmonic

K.	The Monitor shall have a standard 4-year warranty.

L.	Acceptable product is Electro Industries / Gaugetech, Model 3DVA120.

- Add the following suffixes for added options:

a.	(-H) - Harmonics Option

  - (-NL) - Two Dry Contact Relays

  - (-G) – Direct 480 Volt monitoring

d.	(-K110) - Remote Mounting Kit

e.	(SF232DB) - Digital RS232 port

f.	(SF485AB) - Digital RS485 port

g.	(SNFI-1) - 0-1mA analog output port (4 channels)

h.	(SNFI-20) - 4-20mA analog output port (4 channels)

- For specification information, contact:

Electro Industries/Gaugetech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741