Generic Specification For

Frequency Switchboard Monitoring

## FF Series

2.    	PRODUCT

2.1  	POWER METERS

A.	The Monitor shall accept input from standard potential transformers (120 volt secondary). The monitor shall be capable of connecting to a voltage monitoring range of up to 600 volts, phase to phase. Surge withstand shall conform to IEEE C37.90.1

B.	The Monitor shall have an accuracy of +/- 0.02 Hz (FF60)or better for frequency.

C.	The display shall consist of four digits, (0-9999) and shall use 0.8” Super Large L.E.D.s..

D.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

E.	The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC.

F.	The Monitor shall have a standard 4-year warranty.

G.	Acceptable product shall be from the following Electro Industries/Gaugetech, Model numbers:

## FF60 – (5.0 – 99.99Hz Frequency Range)

## FF400 – (50.0 – 999.9Hz Frequency Range)

## FF1000 – (5.0 – 999.9Hz Frequency Range)

- Add the suffix (-RMS) for true RMS readings, or (-G) for extended input voltage to 600V.

- For specification information, contact:

Electro Industries/Gaugetech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741