Generic Specification For

AC Voltage Switchboard Monitoring

## FVA Series

2.    	PRODUCT

2.1  	POWER METERS

A.	The Monitor shall accept input from a standard instrument transformer (120V input from potential transformers), or direct input up to 600 volts.

- Surge withstand shall conform to IEEE C37.90.1

- The Monitor shall withstand 130% rated voltage.

B.	The Monitor shall have an accuracy of +/- 0.2% or better for voltage.

C.	The display shall consist of four digits, (0-9999) and shall use 0.8” Super Large L.E.D.s.

D.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

E.	The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC.

F.	The Monitor shall have a standard 4-year warranty.

G.	Acceptable product shall be from the following Electro Industries / Gaugetech, Model numbers:

## FVA10 – (9.999V FULL SCALE RANGE)

## FVA100 – (99.99V FULL SCALE RANGE)

## FVA600 – (600.0V FULL SCALE RANGE)

FVA120 – (USE WITH 120V PTs.  SPECIFY SCALING)

- Add the suffix (-RMS) for true RMS readings.

- For specification information, contact:

Electro Industries/Gaugetech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741