Generic Specification For

DC Voltage Switchboard Monitoring

## FVD Series

2.    	PRODUCT

2.1  	POWER METERS

A.	The Monitor shall measure single phase DC voltage up to 600 volts.

- The Monitor shall withstand 200% rated current continuously.

- Surge withstand shall conform to IEEE C37.90.1

B.	The Monitor shall have an accuracy of +/- 0.05% or better for DC voltage.

- The display shall consist of four digits, (0-9999) and shall use 0.8” Super Large L.E.D.s.

D.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

E.	The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC.

F.	The Monitor shall have a standard 4-year warranty.

G.	Acceptable product shall be from the following Electro Industries / Gaugetech, Model numbers:

## FVD10 – (9.999V Full Scale Range)

## FVD100 – (99.99V Full Scale Range)

## FVD600 – (600.0V Full Scale Range)

- For specification information, contact:

Electro Industries/Gaugetech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741