Generic Specification For Accumulated Energy and Demand Monitor

## SBM100

2.    	PRODUCT

2.1  	POWER METERS

A.	The Monitor shall accept input from standard instrument transformers (5A secondary current transformers and 120 volt secondary potential transformers). The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.

- The Monitor shall withstand 200% rated current continuously. It shall withstand 10X rated current for at least 3 seconds.

- The Monitor shall be capable of connection to a three phase, four wire wye system or a three phase, three wire, open delta system.

- Surge withstand shall conform to IEEE C37.90.1

- The Monitor shall be user programmable to any PT or CT ratio.  DIP switches or other fixed ratio designs shall not be acceptable.

- PTs and CTs shall be physically connected on the secondary side.

- Voltage and current connections shall be segregated from each other on the front of the monitor to provide safe connections.

- The monitor shall store all data in a non-volatile Eeprom. No battery is needed to store data in event of power down.

B.	The Monitor shall have an accuracy of +/- 0.4% or better for wattage.

- The Monitor must measure true RMS watts, watt-hours, and watt demand, and shall have separate positive and negative watt-hour accumulators

C.	The Monitor must use 0.56” L.E.D. displays.  There must be one line of display that can optionally show watts, watt-hours, and watt demand. Watt/hr resolution shall be to 6 ½ digits. No multiplier factors are needed.

D.	The monitor shall include output options for pulse outputs and relay/alarm outputs.

- The Monitor shall have two form C, dry contact relay outputs for alarm or control and 1 KYZ pulse output related to Watts/HR.

- The Monitor must be capable of tripping its dry contact outputs for over/under Wattage, both positive and negative

E.	The Monitor shall have the capability of utilizing a RS485 port for digital communications using EI Protocol or Modbus Protocol.

- The Monitor shall have the capability of having up to 9999 separate addresses for multi-point communication.

- The digital port connections shall be separated from the voltage and current connections.

F.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a NEMA rated 4x enclosure suitable for surface mounting.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

G.	The Monitor shall support control power options for 120 VAC.

H.	The Monitor shall have a standard 4-year warranty.

I.	Acceptable product is Electro Industries / GaugeTech, Model SBM100.

Add the following suffixes for added options:

      - (RS485) - RS485 with Modbus Communication

      - (NL) – 2 Relay Outputs and 1 KYZ Pulse

      - (CT200K) - .94” Window, 200 Amps, 3 CTs

      - (CT400K)  - 1.25 Window, 400 Amps, 3 CTs

      - (CT800K)  - 2.06” Window, 800 Amps, 3 CTs

      - (CT2000K) – 3” Window, 2000 Amps, 3 CTs

- For specification information, contact:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741