Generic Specification For

Multifunction Electrical Power Monitor

## DMVA100

2.    	PRODUCT

2.1  	POWER METERS

A.	The Monitor shall be UL listed and CE marked.

B.	The Monitor shall accept input from standard instrument transformers (5A secondary current transformers and 120 volt secondary potential transformers). The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.

- The Monitor shall withstand 200% rated current continuously. It shall withstand 10X rated current for at least 3 seconds.

- The Monitor shall be capable of connection to a three phase, four wire wye system or a three phase, three wire, open delta system.

- Surge withstand shall conform to IEEE C37.90.1

- The Monitor shall be user programmable to any PT or CT ratio. DIP switches or other fixed ratio designs shall not be acceptable.

- Voltage and current connections shall be segregated from each other on the back of the monitor to provide safe connections.

C.	The Monitor shall have an accuracy of +/- 0.2% or better for volts and amps and 0.2 Hz for frequency.

- The Monitor shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral; and frequency.

- The Monitor must be capable of providing readings for both instantaneous and average readings.

- The Monitor shall monitor max/min average demand values for all current readings. The demand interval shall be user programmable.

D.	The monitor shall include a two or three line, integrated, light-emitting diode (LED) display.

- The Monitor must have one line of display for voltage readings and a separate line of display for current readings.  Optional frequency readings must be mounted on a third line of display.

- The display must be 0.56” LED’s on each of the 3 separate lines.

- The Monitor must be capable of displaying one leg of volts, amps and frequency simultaneously.

E.	The monitor shall include output options for relay/alarm outputs.

- The Monitor shall have two form C dry contact relay outputs for alarm or

control.

- The Monitor must be capable of tripping its dry contact outputs for the following conditions:

  Over/Under Voltage - Phase to Neutral and Phase to Phase

  Over/Under Current - Phases A, B, C and Neutral

  Voltage Phase Reversals

  Voltage Imbalance

  Over/Under Frequency

F.	The monitor shall be microprocessor based and shall be fully user programmable.

- The Monitor must store 3 separate copies of the critical setup data in a write protected EEPROM. All 3 copies of the critical data must have independent checksums.

- The Monitor shall be configured through the front panel or through a computer interface. It shall not be necessary to dismantle the monitor to perform programming functions.

- Configuration data shall be password protected.

G.	The monitor shall be capable of utilizing either an RS232 or RS485 digital communications port.

- The Monitor shall have the capability of utilizing either an RS232 or RS485 port for digital communications using an open ASCII-based protocol.

2.	The Monitor shall have the capability of having up to 9999 separate addresses for multi-point communication.

- The digital port connections shall be separated from the voltage and current connections.

H.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable.

- The Monitor shall have a separable input module which can be remote mounted up to 3 feet from the display mounting.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

I.	The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC.

J.	The Monitor shall have a standard 4-year warranty.

K.	Acceptable product is Electro Industries / Gaugetech, Model DMVA100.

- Add the following suffixes for added options:

a.	(-F) – Frequency Measurement

b.	(-G) - Direct voltage monitoring to 600 volts phase to phase

c.	(-NL) - Two Form C Dry Contact Relays

d.	(-K110) - Remote Mounting Kit

e.	(SF232DB) - Digital RS232 port

f.	(SF485DB) - Digital RS485 port

- For specification information, contact:

Electro Industries/Gaugetech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741