EIG-Register Mappings for MODBUS Protocol

Including Long Island Lighting Company Utility Standard Mappings

FOR ELECTRO INDUSTRIES/GAUGETECH POWER MONITORING DEVICES

Futura+ Series

DM Series

Release Date: December 28, 1998

Version: 1.4/12-98

METER PROFILE BLOCK		Page 3

METER INFORMATION BLOCK								Page 3

PROGRAMMING DATA BLOCK								Page 3

PHASE REVERSAL/IMBALANCE BLOCK							Page 4

DAXI DATA BLOCK									Page 4

HOUR BLOCK										Page 5

LIMIT DETECTION BLOCK								Page 5

RELAY STATUS BLOCK									Page 5

THD SUMMARY BLOCK									Page 6

THD DETAIL BLOCK									Page 6

HARM VOLT A Registers								Page 6

HARM VOLT B Registers			Page 6

HARM VOLT C Registers								Page 6

HARM AMP A Registers								Page 6

HARM AMP B Registers								Page 6

HARM AMP C Registers								Page 6

RESET BLOCK										Page 7

COMMUNICATION PARAMETERS							Page 7

APPENDIX A:  PROGRAMMING DATA BLOCK MAP					Page 8

CONFIGURATION INFORMATION					                	Page 9

Interval									                	Page 9

Address	Page 9

Baud Rate								                	Page 9

Config									                	Page 9

VOLTS Full Scale								                	Page 10

AMPS Full Scale								                	Page 10

DECIMAL PLACEMENT & LILCO CONFIGURATION			                	Page 10

LILCO CONFIGURATION						                	Page 10

SET ABOVE/BELOW LIM 1					                               		Page 10

SET ABOVE/BELOW LIM 2						                	Page 10

VOLTS AN Lim 1-FREQ Lim 2						                	Page 11

RLY LIM 1								               		Page 11

RLY LIM 2-RLY2 LIM2							               		Page 11

DELAY ON RLY 1-2							                	Page 11

SAB THD LIM 1-2							                	Page 11

RLY THD LIM 1-2							               		Page 11

RLY2 THD LIM 1-2							                	Page 11

THD VOLTS A LIM 1 - THD AMPS C LIM2					                	Page 11

RLY 1-2 IMB LIM 1						 	Page 12

IMB LIM 1								                	Page 12

RELAY 1 MODE								               		Page 12

RELAY 2 MODE								                	Page 12

Delay off RLY 1-2								                	Page 12

KYZ MAP, KYZ FACTOR							                	Page 13

CT/PT Ratios								                	Page 13

SYSTEM RESET								                	Page 13

APPENDIX B:  LILCO MAPPING						                	Page 14

SYSTEM SANITY							                	Page 14

OLLING VALUES						                                	Page 15

NEUTRAL CURRENT						                	Page 15

HOUR READINGS						                	Page 15

FREQUENCY							                	Page 15

ENERGY RESET							                	Page 15

APPENDIX C:  FLOATING POINT REGISTERS	 	Page 16

NEGATIVE MAX/MIN BLOCK						                	Page 16

FLOATING POINT-DAXI DATA BLOCK					                	Page 16/17

FLOATING POINT-NEGATIVE MAX/MIN BLOCK				                	Page 17

FLOATING POINT-THD DETAIL BLOCK					                	Page 18

APPENDIX D: MASS MEMORY & NULL TERMINATED HOUR READINGS	                	Page 19

EXCEPTION FLAGS 							                	Page 20

METER PROFILE BLOCK

| Registers |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 0000 | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40001 |
|  | W |  |  | VAR |  |  | VA |  |  | PF |  |  |  |  |  |  |  |
| 0001 | A | B | C | A | B | C | A | B | C | A | B | C | REV | IMB | ---- | ---- | 40002 |
|  | KF VOLTS |  |  | KF AMPS |  |  |  |  |  |  |  |  | HOUR |  |  |  |  |
| 0002 | A | B | C | A | B | C | ---- | ---- | D | A | X | I | W | VAR | VA | ---- | 40003 |
|  | THD VOLTS |  |  | THD AMPS |  |  |  |  | HARM VOLTS |  |  | HARM AMPS |  |  |  |  |  |
| 0003 | A | B | C | A | B | C | ---- | ---- | A | B | C | A | B | C | ---- | ---- | 40004 |
| LIMITS |  | RELAYS |  | KYZ |  |
| 0004 | 1 | 2 | --- | --- | 1 | 2 | 3 | --- | 1 CH | 3 CH | ---- | ---- | ---- | ---- | ---- | ---- | 40005 |
| 0005+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40006+ |

RELAY AND KYZ:

A bit value of 1 means that the firmware supports features, but specific hardware is necessary for those

features to operate.  The hardware is only installed if the appropriate options are purchased for the meter.

THESE BITS DO NOT GUARANTEE THESE FEATURES.  A bit value of 0 means the features are not

supported.

Other: 	A bit value of 1 means the features are supported.

METER INFORMATION BLOCK

| Registers |  |  |  |  |  |  |  | Registers |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0 |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  |  |
|  | METER NAME |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0008+ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40009+ |
|  | METER NAME |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0010+ |  |  |  |  | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  | 40017+ |
| 0018+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40025+ |
|  |  |  |  |  |  |  |  |  |  |  | VERSION NUMBERS |  |  |  |  |  |  |
| 0020+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  | MODBUS |  | ANALOG |  | DIGITAL |  | 40033+ |

Registers 0008-0011:

24 Bytes ASCII, containing the meter name, left justified and padded with ASCII SPACEs (0x20)

Registers 0025-0027:

2 Bytes each two’s compliment number, representing a version number with a single implied decimal point.

PROGRAMMING DATA BLOCK

| Registers |  |  |  |  |  |  |  | Registers |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0 |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  |  |
| 0028+ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40041+ |
| ¦ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ¦ |
| 010C+ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40269+ |

Registers 0028-0113:

Until written to, the Programming Data Block contains information accurate to the current operation

of the meter.  Changes written to the Programming Data Block do not go into effect until a system reset is

requested through communication.

See Appendix A: Programming Data Block for specific information.

PHASE REVERSAL / IMBALANCE BLOCK

| Registers |  | Registers |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- |
|  | PHASE REVERSAL |  |  |  |  |  |
| 0114 |  |  |  |  |  | 40277 |
|  | PHASE IMBALANCE |  |  |  |  |  |
| 0115 |  |  |  |  |  | 40278 |

Register 0114: A 2 Byte value of 0 x 0000 means a phase sequence of A-B-C.

A 2-Byte non-zero value means a phase sequence of C-B-A.

## Register 0115: 2 Byte two’s compliment number, representing a percentage

with a single implied decimal place.

DAXI DATA BLOCK

Registers   584/984    Registers   584/984    Registers   584/984   Registers   584/984

|  | INST (D) |  |  | AVE (A) |  |  | MAX (X) |  |  | MIN (I) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VOLT AN | 0116 |  | 40279 | 013D |  | 40318 | 0164 |  | 40357 | 018B |  | 40396 |
| VOLT BN | 0117 |  | 40280 | 013E |  | 40319 | 0165 |  | 40358 | 018C |  | 40397 |
| VOLT CN | 0118 |  | 40281 | 013F |  | 40320 | 0166 |  | 40359 | 018D |  | 40398 |
| VOLT AB | 0119 |  | 40282 | 0140 |  | 40321 | 0167 |  | 40360 | 018E |  | 40399 |
| VOLT BC | 011A |  | 40283 | 0141 |  | 40322 | 0168 |  | 40361 | 018F |  | 40400 |
| VOLT CA | 011B |  | 40284 | 0142 |  | 40323 | 0169 |  | 40362 | 0190 |  | 40401 |
| AMP A | 011C |  | 40285 | 0143 |  | 40324 | 016A |  | 40363 | 0191 |  | 40402 |
| AMP B | 011D |  | 40286 | 0144 |  | 40325 | 016B |  | 40364 | 0192 |  | 40403 |
| AMP C | 011E |  | 40287 | 0145 |  | 40326 | 016C |  | 40365 | 0193 |  | 40404 |
| AMP N | 011F |  | 40288 | 0146 |  | 40327 | 016D |  | 40366 | 0194 |  | 40405 |
| WATT | 0120 |  | 40289 | 0147 |  | 40328 | 016E |  | 40367 | 0195 |  | 40406 |
| VAR | 0121 |  | 40290 | 0148 |  | 40329 | 016F |  | 40368 | 0196 |  | 40407 |
| VA | 0122 |  | 40291 | 0149 |  | 40330 | 0170 |  | 40369 | 0197 |  | 40408 |
| PF | 0123 |  | 40292 | 014A |  | 40331 | 0171 |  | 40370 | 0198 |  | 40409 |
| FREQ | 0124 |  | 40293 | 014B |  | 40332 | 0172 |  | 40371 | 0199 |  | 40410 |
| WATT A | 0125 |  | 40294 | 014C |  | 40333 | 0173 |  | 40372 | 019A |  | 40411 |
| WATT B | 0126 |  | 40295 | 014D |  | 40334 | 0174 |  | 40373 | 019B |  | 40412 |
| WATT C | 0127 |  | 40296 | 014E |  | 40335 | 0175 |  | 40374 | 019C |  | 40413 |
| VAR A | 0128 |  | 40297 | 014F |  | 40336 | 0176 |  | 40375 | 019D |  | 40414 |
| VAR B | 0129 |  | 40298 | 0150 |  | 40337 | 0177 |  | 40376 | 019E |  | 40415 |
| VAR C | 012A |  | 40299 | 0151 |  | 40338 | 0178 |  | 40377 | 019F |  | 40416 |
| VA A | 012B |  | 40300 | 0152 |  | 40339 | 0179 |  | 40378 | 01A0 |  | 40417 |
| VA B | 012C |  | 40301 | 0153 |  | 40340 | 017A |  | 40379 | 01A1 |  | 40418 |
| VA C | 012D |  | 40302 | 0154 |  | 40341 | 017B |  | 40380 | 01A2 |  | 40419 |
| PF A | 012E |  | 40303 | 0155 |  | 40342 | 017C |  | 40381 | 01A3 |  | 40420 |
| PF B | 012F |  | 40304 | 0156 |  | 40343 | 017D |  | 40382 | 01A4 |  | 40421 |
| PF C | 0130 |  | 40305 | 0157 |  | 40344 | 017E |  | 40383 | 01A5 |  | 40422 |
| KF VOLT A | 0131 |  | 40306 | 0158 |  | 40345 | 017F |  | 40384 | 01A6 |  | 40423 |
| KF VOLT B | 0132 |  | 40307 | 0159 |  | 40346 | 0180 |  | 40385 | 01A7 |  | 40424 |
| KF VOLT C | 0133 |  | 40308 | 015A |  | 40347 | 0181 |  | 40386 | 01A8 |  | 40425 |
| KF AMP A | 0134 |  | 40309 | 015B |  | 40348 | 0182 |  | 40387 | 01A9 |  | 40426 |
| KF AMP B | 0135 |  | 40310 | 015C |  | 40349 | 0183 |  | 40388 | 01AA |  | 40427 |
| KF AMP C | 0136 |  | 40311 | 015D |  | 40350 | 0184 |  | 40389 | 01AB |  | 40428 |
| R E S E R V E D | 0137 |  | 40312 | 015E |  | 40351 | 0185 |  | 40390 | 01AC |  | 40429 |
| R E S E R V E D | 0138 |  | 40313 | 015F |  | 40352 | 0186 |  | 40391 | 01AD |  | 40430 |
| R E S E R V E D | 0139 |  | 40314 | 0160 |  | 40353 | 0187 |  | 40392 | 01AE |  | 40431 |
| R E S E R V E D | 013A |  | 40315 | 0161 |  | 40354 | 0188 |  | 40393 | 01AF |  | 40432 |
| R E S E R V E D | 013B |  | 40316 | 0162 |  | 40355 | 0189 |  | 40394 | 01B0 |  | 40433 |
| R E S E R V E D | 013C |  | 40317 | 0163 |  | 40356 | 018A |  | 40395 | 01B1 |  | 40434 |

Registers 0116-01B1: 2 Byte two’s compliment numbers.  Decimal placement and scales for appropriate readings are available

from the Programming Data Block.

HOUR BLOCK

| Registers |  |  |  |  |  |  |  | Registers |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0 |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  |  |
|  | WATT HOUR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 01B2+ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40435+ |
|  | VAR HOUR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 01BA+ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40443+ |
|  | VA HOUR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 01C2+ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40451+ |

Register 501B2-01C9:

16 Bytes each ASCII, representing a 16 Byte BCD count of the base Hour function.  (Decimal placement and scales

for the appropriate readings are available from within the Programming Data Block.  See Appendix A: Programming

Data Block Map, Config, bits KV and MW).

# LIMIT DETECTION BLOCK

| Registers |  |  |  |  |  |  | Limit 1 Bits |  |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  |  |  |  |  |  |  |  |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 01CA | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | A | B | C | A | B | C | REV | IMB | 40459 |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 01CB | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40460 |
| 01CC+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40461+ |
| Registers |  |  |  |  |  |  | Limit 2 Bits |  |  |  |  |  |  |  |  |  | 584/984 |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  |  |  |  |  |  |  |  |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 01CE | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | A | B | C | A | B | C |  |  | 40463 |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 01CF | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40464 |
| 01D0+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40465+ |

Register 501CA-01CF:

A bit value of 1 means that the limit is being exceeded for the associated quantity.

A bit value of 0 means that the limit is not being exceeded for the associated quantity.

RELAY STATUS BLOCK

| Registers |  |  |  |  |  |  | Relay 1 Bits |  |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  |  |  |  |  |  |  | STATUS |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 01DA | ---- | ---- | ---- | ---- | ---- | ---- | ON | LK | A | B | C | A | B | C | REV | IMB | 40475 |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 01DB | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40476 |
| 01DC+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40477+ |
| Registers |  |  |  |  |  |  | Relay 2 Bits |  |  |  |  |  |  |  |  |  | 584/984 |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  |  |  |  |  |  |  | STATUS |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 01DE | ---- | ---- | ---- | ---- | ---- | ---- | ON | LK | A | B | C | A | B | C | REV | IMB | 40479 |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 01DF | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40480 |
| 01E0+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40481+ |

_____________________________________________________________________________________________________________

| Registers |  |  |  |  |  |  | Relay 3 Bits |  |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  |  |  |  |  |  |  | STATUS |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 01E2 | ---- | ---- | ---- | ---- | ---- | ---- | ON | LK | A | B | C | A | B | C | REV | IMB | 40483 |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 01E3 | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40484 |
| 01E0+ | R E S E R V E D F O R F U T U R E U S E |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 40485+ |

Registers 01DA-01E3:

Status: A bit value of 1 for ON means the relay is activated, 0 means not activated.

A bit of 1 for LK means the relay is locked, 0 means not locked.

Other: A bit value of 1 means the associated limit has activated the relay.

A bit value of 1 means the associated limit has not activated the relay.

THD SUMMARY BLOCK

|  | Registers |  | 584/984 | Registers |  | 584/984 | Registers |  | 584/984 | Registers |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | INST (D) |  |  |  |  |  | MAX (X) |  |  | MIN (I) |  |  |
| THD VOLT A | 01EA |  | 40491 | R E S E R V E D |  |  | 01F6 |  | 40503 | 01FC |  | 40509 |
| THD VOLT B | 01EB |  | 40492 | R E S E R V E D |  |  | 01F7 |  | 40504 | 01FD |  | 40510 |
| THD VOLT C | 01EC |  | 40493 | R E S E R V E D |  |  | 01F8 |  | 40505 | 01FE |  | 40511 |
| THD AMP A | 01ED |  | 40494 | R E S E R V E D |  |  | 01F9 |  | 40506 | 01FF |  | 40512 |
| THD AMP B | 01EE |  | 40495 | R E S E R V E D |  |  | 01FA |  | 40507 | 0200 |  | 40513 |
| THD AMP C | 01EF |  | 40496 | R E S E R V E D |  |  | 01FB |  | 40508 | 0201 |  | 40514 |

Registers 01EA-0201:

2 Byte each two’s compliment numbers, representing a percentage with a single decimal point.

THD DETAIL BLOCK

HARM VOLT A Registers

|  |  | Registers |  |  | 584/984 | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | PERCENT |  |  |  | PHASE |  |  |  |
|  | HARM 0 | 0202 |  |  | 40515 | 0203 |  |  | 40516 |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 0240 |  |  | 40577 | 0241 |  |  | 40578 |
|  |  | 0242+ | RESERVED FOR FUTURE USE |  |  |  |  |  | 40579+ |

HARM VOLT B Registers

|  | HARM 0 | 0282 |  |  | 40643 | 0283 |  |  | 40644 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 02C0 |  |  | 40705 | 02C1 |  |  | 40706 |
|  |  | 02C2+ | RESERVED FOR FUTURE USE |  |  |  |  |  | 40707+ |

HARM VOLT C Registers

|  | HARM 0 | 0302 |  |  | 40771 | 0303 |  |  | 40772 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 0340 |  |  | 40833 | 0341 |  |  | 40834 |
|  |  | 0342+ | RESERVED FOR FUTURE USE |  |  |  |  |  | 40835+ |

HARM AMP A Registers

|  | HARM 0 | 0382 |  |  | 40899 | 0383 |  |  | 40900 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 03C0 |  |  | 40961 | 03C1 |  |  | 40962 |
|  |  | 03C2+ | RESERVED FOR FUTURE USE |  |  |  |  |  | 40963+ |

HARM AMP B Registers

|  | HARM 0 | 0402 |  |  | 41027 | 0403 |  |  | 41028 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 0440 |  |  | 41089 | 0441 |  |  | 41090 |
|  |  | 0442+ | RESERVED FOR FUTURE USE |  |  |  |  |  | 41091+ |

HARM AMP C Registers

|  | HARM 0 | 0482 |  |  | 41155 | 0483 |  |  | 41156 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 04C0 |  |  | 41217 | 04C1 |  |  | 41218 |
|  |  | 04C2+ | RESERVED FOR FUTURE USE |  |  |  |  |  | 41219+ |

Register 0202-04C1:

Percent: 2 Bytes each two’s compliment number, representing a percentage with a single implied decimal point.

Phase:   2 Bytes each two’s compliment number, representing a phase angle with a single implied decimal point.

RESET BLOCK

| Registers |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 0502 | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 41283 |
|  | W |  |  | VAR |  |  | VA |  |  | PF |  |  |  |  |  |  |  |
| 0503 | A | B | C | A | B | C | A | B | C | A | B | C | ---- | ---- | ---- | ---- | 41284 |
|  | KF VOLTS |  |  | KF AMPS |  |  |  |  |  |  | RESET |  | HOUR |  |  |  |  |
| 0504 | A | B | C | A | B | C | ---- | ---- | ---- | ---- | X | I | W | VAR | VA | ---- | 41285 |
|  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0505 | A | B | C | A | B | C | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | 41286 |
| 0506+ | RESERVED FOR FUTURE USE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 41287+ |

Registers 0502-0505:

Rest: A bit of 1 for X or I will reset the MAX or MIN, respectively, of indicated features.

The bits from indicated features will be cleared as their feature is reset.

Hour: A bit value of 1 for W, VAR, or VA will reset the WATT, VAR, or VA Hour counter.

Other: A bit value will reset the MAX or MIN of the associated feature upon setting either the X or I bit in the Reset Group.

COMMUNICATION PARAMETERS

Electro Industries meters with the MODBUS communication option can communicate with either ASCII or RTU framing.

ASCII framing - 7 data bits, even parity, 1 stop bit

RTU framing - 8 data bits, no parity, 1 stop bits

User selection of this parameter can be accomplished either through communication

(See Appendix A: Programming Data Block   Map) or by the user through the keypad.

Keypad selection is accomplished through the Programming mode in the System Configuration function,

Group 0, Function 3. Switch PACK 2 Position C controls which framing mode to use for MODBUS communication.

Switch setting 0 signifies RTU framing, while switch settings 1 signifies ASCII framing.

For a detailed explanation of the Programming Mode, see the Programming Manual.

MODBUS communication for Electro Industries meters is limited to 50 registers per query.

_____________________________________________________________________________________________________________

APPENDIX A:  PROGRAMMING DATA BLOCK MAP

| Registers |  |  |  | Registers |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0 |  | 1 |  | 2 |  | 3 |  |  |
| 0028+ | Interval |  | Address |  | Baud Rate |  | Config |  | 40041+ |
| 002C+ | VOLTS Full Scale |  | AMPS Full Scale |  | Decimal Placement |  | LILCO |  | 40045+ |
| 0030+ | Set Above/Below Lim1 |  | Set Above/Below Lim2 |  | VOLTS AN Lim1 |  | VOLTS AN Lim2 |  | 40049+ |
| 0034+ | AMPS A Lim1 |  | AMPS A Lim2 |  | VOLTS BN Lim1 |  | VOLTS BN Lim2 |  | 40053+ |
| 0038+ | AMPS B Lim1 |  | AMPS B Lim2 |  | VOLTS CN Lim1 |  | VOLTS CN Lim2 |  | 40057+ |
| 003C+ | AMPS C Lim1 |  | AMPS C Lim2 |  | VOLTS AB Lim1 |  | VOLTS AB Lim2 |  | 40061+ |
| 0040+ | VOLTS BC Lim1 |  | VOLTS BC Lim2 |  | VOLTS CA Lim1 |  | VOLTS CA Lim2 |  | 40065+ |
| 0044+ | AMPS N Lim1 |  | AMPS N Lim2 |  | WATT Lim1 |  | WATT Lim2 |  | 40069+ |
| 0048+ | VAR Lim1 |  | VAR Lim2 |  | VA Lim1 |  | VA Lim2 |  | 40073+ |
| 004C+ | PF Lim1 |  | PF Lim2 |  | FREQ Lim1 |  | FREQ Lim2 |  | 40077+ |
| 0050+ |  |  |  |  |  |  |  |  | 40081+ |
| 0054+ |  |  |  |  |  |  |  |  | 40085+ |
| 0058+ |  |  |  | R E S E R V E D |  |  |  |  | 40089+ |
| 005C+ |  |  |  | F O R |  |  |  |  | 40093+ |
| 0060+ |  |  |  | F U T U R E |  |  |  |  | 40097+ |
| 0064+ |  |  |  | U S E |  |  |  |  | 40101+ |
| 0068+ |  |  |  |  |  |  |  |  | 40105+ |
| 006C+ |  |  |  |  |  |  |  |  | 40109+ |
| 0070+ | RLY1 Lim1 |  | RLY1 Lim2 |  | RLY2 Lim1 |  | RLY2 Lim2 |  | 40113+ |
| 0074+ | Delay on RLY1-2 |  | SAB THD Lim1-2 |  | RLY1 THD Lim1-2 |  | RLY2 THD Lim1-2 |  | 40117+ |
| 0078+ | THD VOLTS A Lim1 |  | THD VOLTS A Lim2 |  | THD AMPS A Lim1 |  | THD AMPS A Lim2 |  | 40121+ |
| 007C+ | THD VOLTS B Lim1 |  | THD VOLTS B Lim2 |  | THD AMPS B Lim1 |  | THD AMPS B Lim2 |  | 40125+ |
| 0080+ | THD VOLTS C Lim1 |  | THD VOLTS C Lim2 |  | THD AMPS C Lim1 |  | THD AMPS C Lim2 |  | 40129+ |
| 0084+ | RLY1-2 IMB Lim1 |  | IMB Lim1 |  | RELAY 1 MODE |  |  |  | 40133+ |
| 0088+ | RELAY 2 MODE |  |  |  | Delay off RLY1-2 |  | KYZ MAP |  | 40137+ |
| 008C+ | KYZ MAP | KYZ FACTOR |  |  |  |  |  |  | 40141+ |
| 0090+ |  |  |  |  |  |  |  |  | 40145+ |
| 0094+ |  |  |  |  |  |  |  |  | 40149+ |
| 0098+ |  |  |  |  |  |  |  |  | 40153+ |
| 009C+ |  |  |  |  |  |  |  |  | 40157+ |
| 00A0+ |  |  |  |  |  |  |  |  | 40161+ |
| 00A4+ |  |  |  |  |  |  |  |  | 40165+ |
| 00A8+ |  |  |  |  |  |  |  |  | 40169+ |
| 00AC+ |  |  |  |  |  |  |  |  | 40173+ |
| 00B0+ |  |  |  |  |  |  |  |  | 40177+ |
| 00B4+ |  |  |  |  |  |  |  |  | 40181+ |
| 00B8+ |  |  |  |  |  |  |  |  | 40185+ |
| 00BC+ |  |  |  |  |  |  |  |  | 40189+ |
| 00C0+ |  |  | R E S E R V E D |  |  |  |  |  | 40193+ |
| 00C4+ |  |  | F O R |  |  |  |  |  | 40197+ |
| 00C8+ |  |  | F U T U R E |  |  |  |  |  | 40201+ |
| 00CC+ |  |  | U S E |  |  |  |  |  | 40205+ |
| 00D0+ |  |  |  |  |  |  |  |  | 40209+ |
| 00D4+ |  |  |  |  |  |  |  |  | 40213+ |
| 00D8+ |  |  |  |  |  |  |  |  | 40217+ |
| 00DC+ |  |  |  |  |  |  |  |  | 40221+ |
| 00E0+ |  |  |  |  |  |  |  |  | 40225+ |
| 00E4+ |  |  |  |  |  |  |  |  | 40229+ |
| 00E8+ |  |  |  |  |  |  |  |  | 40233+ |
| 00EC+ |  |  |  |  |  |  |  |  | 40237+ |
| 00F0+ |  |  |  |  |  |  |  |  | 40241+ |
| 00F4+ |  |  |  |  |  |  |  |  | 40245+ |
| 00F8+ |  |  |  |  |  |  |  |  | 40249+ |
| 00FC+ |  |  |  |  |  |  |  |  | 40253+ |
| 0100+ |  |  |  |  |  |  |  |  | 40257+ |
| 0104+ |  |  |  |  |  |  |  |  | 40261+ |
| 0108+ | CT Ratio |  | PT Ratio |  |  |  |  |  | 40265+ |
| 010C+ |  |  |  |  |  |  |  |  | 40269+ |
| 0110+ |  |  |  |  |  |  | SYSTEM RESET |  | 40273+ |

CONFIGURATION INFORMATION

Interval

Register 0028:

2 Byte two’s compliment number representing the Integration Interval in seconds.

Address

Register 0029:

2 Byte two’s compliment number, which is the Address of the meter for communication purposes.

Under MODBUS communications, this address should be between 1 and 247, inclusive,  These limits

may be different for other communication protocols.

Baud Rate

Register 002A:

2 Byte two’s compliment number, which is the Baud Rate being used for communications.  Only baud rate

valid for the meter in question should be used (e.g., 1200, 9600).  Improper settings could disable communication.

Config

|  | Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | 002B | KV | KA | MW | REV | LZ | RST | ---- | DLT | AVG | ---- | ASCII | MOD | RLY1 | RLY2 | COM | DC | 40044 |
| Register 002B: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

KV: A bit value of 1 means the meter is configured for kilovolt inputs.*

A bit value of 0 means the meter is configured for volt inputs.*

KA: A bit value of 1 means the meter is configured for kiloamp inputs.*

A bit value of 0 means the meter is configured for amps inputs. *

MW: A bit value of 1 means the meter is configured for megawatt inputs. *

A bit value of 0 means the meter is configured for kilowatt inputs. *

REV: A bit value of 1 means the Phase Reversal Limits are enabled.

A bit value of 0 means the Phase Reversal Limits are not enabled.

LZ: A bit value of 1 means leading zeros are blanked on the meter display.

A bit value of 0 means leading zeros are displayed on the meter display.

RST: A bit value of 1 means that Reset Protection is enabled.  (Resetting max/min and hour function readings from the

keypad requires the entry of a password).

A bit value of 0 means that Reset Protection is disabled. (Resetting hour function readings from the keypad requires the

entry of a password).

DLT:	 A bit value of 1 means the meter is set up for Open Delta.

A bit value of 0 means the meter is set up for non Open Delta configuration.

AVG:	A bit value of 1 means Limits are set by the Average Readings.

A bit value of 0 means Limits are set by the Instantaneous Readings.

ASCII:	             ASCII      MOD      PROTOCOL

MOD:                   	0	0             Electro Industries

0	1             Modbus RTU

1	0             DNP 3.0

1	1             Modbus ASCII

RLY1:	Please see the Programming Manual about PACK 3 of Function 0, Group 3 for an explanation of the meaning of these bits.

RLY2:	Please see the Programming Manual about PACK 3 of Function 0, Group 3 for an explanation of the meaning of these bits.

COM:	Please see the Programming Manual about PACK 3 of Function 0, Group 3 for an explanation of the meaning of these bits.

DC:      Please see the Programming Manual about PACK 3 of Function 0, Group 3 for an explanation of the meaning of these bits.

These features duplicate those available in the switch PACKS of Function 0, Group 3, in the meter’s Programming Mode.

For further information, please see the other manuals for the meter.

Should these features be changed, a replacement Bezel should be ordered to reflect the new units.

VOLTS Full Scale

Register 002C:

2 Byte two’s compliment number representing the Full Scale for voltage.  For decimal placement, see Decimal Placement below.

AMPS Full Scale

Register 002D:

2 Byte two’s compliment number representing the Full Scale for current. For decimal placement, see Decimal Placement below.

DECIMAL PLACEMENT & LILCO CONFIGURATION

| Registers |  |  |  |  |  |  |  | Registers |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 0 |  |  |  |  |  |  |  | 1 |  |  |  |  |
| 002E+ | VOLTS DP |  |  |  | AMPS DP |  |  |  | WATT DP |  |  |  | LILCO CONFIG |  |  |  | 40047+ |

Registers 002E-002F:

LILCO CONFIGURATION

| Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 7 |  | 6 |  | 5 |  | 4 |  | 3 |  | 2 |  | 1 |  | 0 |  |  |
|  | VOLT |  | AMP |  |  |  | POWER |  |  |  |  |  |  |  | CONFIG |  |  |
| 002F | Round by 10 |  | Current Scale |  |  |  | Power Scale |  |  |  |  |  |  |  | LILCO |  | 40048 |

Register 002F:

These settings effect readings in the LILCO mapping.

Round by 10:	    0=no rounding		 1=round raw readings down by 10 before scaling.

Current Scale:	  00=1A Full Scale	 01=2.5A Full Scale

10= 5A Full Scale	 11=7.5A Full Scale

Power Scale:	000=250W Full Scale	001=500W Full Scale

010=1000W Full Scale	011=1500W Full Scale

100=2000W Full Scale	101=2500W Full Scale

110=3000W Full Scale	111=3500W Full Scale

LILCO Enable:	  0=Normal Mapping          1=LILCO Mapping (Normal mapping starts at 100)

SET ABOVE/BELOW LIM 1

| Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 0030 | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40049 |

Register 0030:

SET ABOVE/BELOW LIM 2

Register 0031:

_____________________________________________________________________________________________________________

VOLTS AN Lim1-FREQ Lim2

|  | Registers 0032-004F: |  |  |  |
| --- | --- | --- | --- | --- |

RLY LIM 1

| Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | VOLTS |  |  |  |  |  | AMPS |  |  |  | POWER |  |  |  |  |  |  |
| 0070 | AN | BN | CN | AB | BC | CA | A | B | C | N | W | VAR | VA | PF | FQ | ---- | 40113 |

Register 0070:

RLY LIM 2-RLY2 LIM2

Register 0071-0073:

Same as RLY1 Lim 1, but for Relay 2 and Limit 2 where appropriate.

DELAY ON RLY1-2

Register				      	      Bites                        			       584/984

0					1

| 0074 | Relay 1 |  |  |  |  |  |  |  | Relay 2 |  |  |  |  |  |  |  | 40117 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Register 0074:

1 Byte unsigned binary number each, representing the delay time from a relay being reset before it could be set in seconds.                         Valid numbers are 0 to 250.

SAB THD LIM 1-2

| Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | Lim1 |  |  |  |  |  |  |  | Lim2 |  |  |  |  |  |  |  |  |
|  | THD VOLTS |  |  | THD AMPS |  |  |  |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 0075 | A | B | C | A | B | C | ---- | ---- | A | B | C | A | B | C | ---- | ---- | 40118 |

Register 0075:

RLY THD LIM 1-2

| Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | RLY1 Lim1 |  |  |  |  |  |  |  | RLY1 Lim2 |  |  |  |  |  |  |  |  |
|  | THD VOLTS |  |  | THD AMPS |  |  |  |  | THD VOLTS |  |  | THD AMPS |  |  |  |  |  |
| 0076 | A | B | C | A | B | C | ---- | ---- | A | B | C | A | B | C | ---- | ---- | 40119 |

Register 0076:

A bit value of 1 means that the indicated limit of the associated value will trigger a Relay.

A bit value of  means that the indicated limit of associated value will not trigger Relay 1.

RLY2 THD LIM 1-2

Register 0077:

Same as RLY THD Lim 1-2, but for Relay 2.

THD VOLTS A LIM 1 - THD AMPS C LIM2

Registers 0078-0083:

RLY1-2 IMB LIM 1

| Register |  |  |  |  |  |  |  | Bits |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
|  | RLY1 |  |  |  |  |  |  |  | RLY2 |  |  |  |  |  |  |  |  |
| 0084 | REV | IMB | ---- | ---- | ---- | ---- | ---- | ---- | REV | IMB | ---- | ---- | ---- | ---- | ---- | ---- | 40133 |

Register 0084:

REV: A bit value of 1 means that Limit 1 for Phase Reversal will trigger the indicated Relay.

A bit value of 0 means that Limit 1 for Phase Reversal will not trigger the indicated Relay.

Phase Reversal Limit 1 is enabled by the REV bit in Config.

IMB: A bit value of 1 means that Limit 1 for Phase Imbalance will trigger the indicated Relay.

A bit value of 0 means that Limit 1 for Phase Imbalance will not trigger the indicated Relay.

Phase Imbalance Limit 1 is always enabled.

### IMB LIM 1

Register 0085:

2 Byte two’s compliment number, representing the limit threshold for Imbalance.  This number represents a percentage with

a single implied decimal place.  The Imbalance Limit is always set to be passed if the Imbalance percentage is greater than this limit.

RELAY 1 MODE:

| Registers |  |  |  |  |  |  |  | Registers |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 0 |  |  |  |  |  |  |  |  | 1 |  |  |  |  |
| 0086+ | IMB/REV CONTROL |  |  |  | LOGIC CONTROL |  |  |  | SET/ RESET CONTROL |  |  |  |  |  |  |  | 40135+ |

Registers 0086-0087:

IMB/REV/CONTROL:   1 Byte two’s compliment number, where a value of ‘0’ means that Relay 1 is set by Phase Reversal

or Imbalance Limits being exceeded and reset by normal Reversal and Imbalance conditions.  Non-zero values mean that

Relay 1 is reset by Phase Reversal or Imbalance Limits being exceeded and set by normal Reversal and Imbalance conditions.

LOGIC CONTROL:   1 Byte two’s compliment number, where a value ‘0’ means that all Limits triggering Relay 1 should be

added to set or reset the Relay.  Non-zero values means that all Limits triggering Relay 1 should be ORed to set or reset the Relay.

SET RESET CONTROL:   2 one Byte two’s compliment numbers.  Two non-zero values indicate that Relay 1 is normally reset,

and exceeded limit set the Relay.  Two values of zero indicate that Relay 1 is normally set and exceeded limits reset the Relay.

Other combination are reserved for future use.

RELAY 2 MODE

Registers 0088-0089:

Same as RELAY 1 MODE, but for Relay 2.

Delay off RLY1-2

| Registers |  |  |  |  |  |  |  | Bites |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 0 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |
| 008A | Relay 1 |  |  |  |  |  |  |  | Relay 2 |  |  |  |  |  |  |  | 40139+ |

Register 008A:

1 Byte unsigned binary number each, representing the delay time from a relay being set before it could be reset, in seconds.

Valid numbers are from ‘0’ to ‘250’

____________________________________________________________________________________________________________

KYZ MAP, KYZ FACTOR

| Registers |  |  |  |  |  | Registers |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 0 |  |  |  | 1 |  |  |  | 2 |  |  |
|  | KYZ MAP |  |  |  |  |  | KYZ FACTOR |  |  |  |  |  |  |
| 008B+ | Port 1 |  | Port 2 |  | Port3 |  | Port1 |  | Port2 |  | Port3 |  | 40143+ |

Register 008B-008D:
KYZ MAP:	1 Byte two’s compliment numbers, signifying whether which ports should be enabled for KYZ outputs of which functions.                              Valid numbers are:

‘0’ KYZ disabled			‘3’ -Watt Hour KYZ

‘1’ +Watt Hour KYZ		‘4’ +VAR Hour KYZ

‘2’ VA Hour KYZ		‘5’ -VAR Hour KYZ

KYZ FACTOR:	1 Byte two’s compliment numbers, representing the KYZ change in level per Watt for each port. Valid number are:

‘0’ one unit of Full Scale		‘4’ one unit of Full Scale

‘1’ two units if Full Scale		‘5’ half a unit of Full Scale

‘2’ ten units of Full Scale		‘6’ one tenth a unit of Full Scale

‘3’ twenty units of Full Scale	’7’ one twentieth a unit of Full Scale

CT/PT Ratios

| Registers |  |  |  |  |  |  |  | Registers |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 0 |  |  |  |  |  |  |  |  | 1 |  |  |  |  |
| 0108+ | CT Ratio |  |  |  |  |  |  |  | PT Ratio |  |  |  |  |  |  |  | 40265+ |

Registers 0108-0109:

2 bytes, MSB first values.  Displayed in the RTU Block.  User definable format.

SYSTEM RESET

Register 0113:

2 Byte two’s compliment number.  When the meter is reset, this register contains the value ‘-32, 768’, (0x8000).

It is recommended that communication with the meter begin with writing another value to this register.  Thus, the

device communicating would know if the meter was reset (through the keypad, power loss, etc.) by reading this

register and checking for the value ‘-32768’.

Communication can request for a reset of the meter by writing the value ‘-1’ (0xFFFF) to this register.  Any changes made to the Programming Data Block through communication will go into effect only after this reset is performed.  Any other form of reset

will result in the loss of any modifications to the Programming Data since the last meter was reset.

Writing  the value ‘0’ (0x0000) to this register will reset the Programming Data Block, permanently removing any changes made to these registers since the last communication requested reset.

_____________________________________________________________________________________________________________

APPENDIX B: LILCO Mapping

If this mapping is configured by setting the appropriate bit in the LILCO configuration register of the Programming Block,

then all the register addresses shown in the regular mapping are moved down by 100.  For example, Instantaneous Volts

AN is normally accessed in register 0116 (40279).  When LILCO mapping is selected, the old register information is now

stored 100 registers lower, in register 017A (40379).

In addition to the bit which configures the mapping, the LILCO Configuration register contains other bits which provide

scaling options for readings in this alternate mapping.

This register mapping is designed in conjunction with Long Island Lighting Company a proposed standard for utility RTUs.

This is designed to give the maximum efficiency in polling information within the blocks.

SYSTEM SANITY

| Registers |  | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- |
|  | SYSTEM SANITY |  |  |  |  |
| 0000 |  |  |  |  | 40001 |

Register 0000:

2-byte indication of proper operation of meter.  A value of 0x0000 indicates the meter detects it is operating properly.

Any other value is an indication that the meter detects an internal fault.

POLLING VALUES

|  |  | Registers |  | 584/984 |  |  |  | Registers |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | POLLING |  |  |  |  |  | POLLING |  |  |
| AMP A |  | 0001 |  | 40002 |  | WATT A |  | 0009 |  | 40010 |
| AMP B |  | 0002 |  | 40003 |  | WATT B |  | 000A |  | 40011 |
| AMP C |  | 0003 |  | 40004 |  | WATT C |  | 000B |  | 40012 |
| VOLT AN |  | 0004 |  | 40005 |  | VAR A |  | 000C |  | 40013 |
| VOLT BN |  | 0005 |  | 40006 |  | VAR B |  | 000D |  | 40014 |
| VOLT CN |  | 0006 |  | 40007 |  | VAR C |  | 000E |  | 40015 |
| WATT |  | 0007 |  | 40008 |  |  |  |  |  |  |
| VAR |  | 0008 |  | 40009 |  |  |  |  |  |  |

Register 0001-000E:

All registers use the least significant 12 bits as signed magnitude numbers.  All polling values report their magnitude

based on the secondary currents and voltage, not the primaries.  Scaling for these values should be interpreted as follows:

0x0000 (0) = negative Full Scale    0x07FF (2047) = 0    0x0FFF (4096) = positive Full Scale

Full Scale for Voltage is 150 V on the secondary.

Full Scale for Current and Power depends on the settings of the MODBUS RTU Configuration bits in the Programming Block.

CT/PT RATIOS

| Registers |  | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- |
|  | CT RATIO |  |  |  |  |
| 000F |  |  |  |  | 40016 |
|  | PT RATIO |  |  |  |  |
| 0010 |  |  |  |  | 40017 |

Registers 000F - 0010:

These are two byte registers of raw binary data, stored by the meter in the Programming Block.  These registers are MSB binary.

Any value of any format my be used. These values may be modified through the CT/PT Ratio Registers in the Programming Block.

NEUTRAL CURRENT

| Registers |  | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- |
|  | NEUTRAL CURRENT |  |  |  |  |
| 0011 |  |  |  |  | 40018 |

Register 0011:

This register is formatted the same as registers 0001 - 000E.

HOUR READINGS

|  |  |  | Registers |  | 584/984 | Registers |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | High |  |  | Low |  |  |
| +KWatt/hour |  |  | 0012 |  | 40019 | 0013 |  | 40020 |
| -KWatt/hour |  |  | 0014 |  | 40021 | 0015 |  | 40022 |
| +KVAR/hour |  |  | 0016 |  | 40023 | 0017 |  | 40024 |
| -KVAR/hour |  |  | 0018 |  | 40025 | 0019 |  | 40026 |

Register 0012 - 0019:

2 - byte MSB binary numbers.  The registers marked Low contain the values 0x0000 - 0x270F, or 0 - 9999, representing

KiloWatt/hour.  The registers marked High contain the values 0x0000 - 0x270F, or 0 - 9999, representing 10's of MegaWatt/hour.

Together, eight digits of KiloWatt/hour may be read.

# FREQUENCY

| Registers |  | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- |
|  | FREQUENCY |  |  |  |  |
| 001A |  |  |  |  | 40027 |

Register 001A:

This register uses the least significant 12 bits as a signed magnitude number.  Scaling for this values should be interpreted as follows:

0x0000 (0) = 45 Hz or less    0x07FF (2047) = 60 Hz    0x0FFF (4096) = 75 Hz or greater

Register 001B - 0062

These registers are reserved for future use.

ENERGY RESET

| Registers |  | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- |
|  | ENERGY RESET |  |  |  |  |
| 0063 |  |  |  |  | 40100 |

Register 0063:

When a value of 0x0001 is written to this register, the HOUR readings on the meter will be reset.

##### ___________________________________________________________________________________________

##### Appendix C: Floating Point Registers

# NEGATIVE MAX/MIN BLOCK

|  | Registers |  | 584/984 | Registers |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- |
|  | NEG MAX |  |  | NEG MIN |  |  |
| WATT | 050A |  | 41291 | 0516 |  | 41303 |
| VAR | 050B |  | 41292 | 0517 |  | 41304 |
| PF | 050C |  | 41293 | 0518 |  | 41305 |
| WATT A | 050D |  | 41294 | 0519 |  | 41306 |
| WATT B | 050E |  | 41295 | 051A |  | 41307 |
| WATT C | 050F |  | 41296 | 051B |  | 41308 |
| VAR A | 0510 |  | 41297 | 051C |  | 41309 |
| VAR B | 0511 |  | 41298 | 051D |  | 41310 |
| VAR C | 0512 |  | 41299 | 051E |  | 41311 |
| PF A | 0513 |  | 41300 | 051F |  | 41312 |
| PF B | 0514 |  | 41301 | 0520 |  | 41313 |
| PF C | 0515 |  | 41302 | 0521 |  | 41314 |

Registers 01EA-0201:

2 Byte two’s compliment numbers.  Decimal placement and scales for appropriate readings are available from the

Programming Data Block.

FLOATING POINT DAXI DATA BLOCK

Registers   584/984    Registers   584/984    Registers   584/984   Registers   584/984

|  | INST (D) |  |  | AVE (A) |  |  | MAX (X) |  |  | MIN (I) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VOLT AN | 0522 |  | 41315 | 057C |  | 41405 | 05D6 |  | 41495 | 0630 |  | 41585 |
| VOLT BN | 0524 |  | 41317 | 057E |  | 41407 | 05D8 |  | 41497 | 0632 |  | 41587 |
| VOLT CN | 0526 |  | 41319 | 0580 |  | 41409 | 05DA |  | 41499 | 0634 |  | 41589 |
| VOLT AB | 0528 |  | 41321 | 0582 |  | 41411 | 05DC |  | 41501 | 0636 |  | 41591 |
| VOLT BC | 052A |  | 41323 | 0584 |  | 41413 | 05DE |  | 41503 | 0638 |  | 41593 |
| VOLT CA | 052C |  | 41325 | 0586 |  | 41415 | 05E0 |  | 41505 | 063A |  | 41595 |
| AMP A | 052E |  | 41327 | 0588 |  | 41417 | 05E2 |  | 41507 | 063C |  | 41597 |
| AMP B | 0530 |  | 41329 | 058A |  | 41419 | 05E4 |  | 41509 | 063E |  | 41599 |
| AMP C | 0532 |  | 41331 | 058C |  | 41421 | 05E6 |  | 41511 | 0640 |  | 41601 |
| AMP N | 0534 |  | 41333 | 058E |  | 41423 | 05E8 |  | 41513 | 0642 |  | 41603 |
| WATT | 0536 |  | 41335 | 0590 |  | 41425 | 05EA |  | 41515 | 0644 |  | 41605 |
| VAR | 0538 |  | 41337 | 0592 |  | 41427 | 05EC |  | 41517 | 0646 |  | 41607 |
| VA | 053A |  | 41339 | 0594 |  | 41429 | 05EE |  | 41519 | 0648 |  | 41609 |
| PF | 053C |  | 41341 | 0596 |  | 41431 | 05F0 |  | 41521 | 064A |  | 41611 |
| FREQ | 053E |  | 41343 | 0598 |  | 41433 | 05F2 |  | 41523 | 064C |  | 41613 |
| WATT A | 0540 |  | 41345 | 059A |  | 41435 | 05F4 |  | 41525 | 064E |  | 41615 |
| WATT B | 0542 |  | 41347 | 059C |  | 41437 | 05F6 |  | 41527 | 0650 |  | 41617 |
| WATT C | 0544 |  | 41349 | 059E |  | 41439 | 05F8 |  | 41529 | 0652 |  | 41619 |
| VAR A | 0546 |  | 41351 | 05A0 |  | 41441 | 05FA |  | 41531 | 0654 |  | 41621 |
| VAR B | 0548 |  | 41353 | 05A2 |  | 41443 | 05FC |  | 41533 | 0656 |  | 41623 |
| VAR C | 054A |  | 41355 | 05A4 |  | 41445 | 05FE |  | 41535 | 0658 |  | 41625 |
| VA A | 054C |  | 41357 | 05A6 |  | 41447 | 0600 |  | 41537 | 065A |  | 41627 |
| VA B | 054E |  | 41359 | 05A8 |  | 41449 | 0602 |  | 41539 | 065C |  | 41629 |
| VA C | 0550 |  | 41361 | 05AA |  | 41451 | 0604 |  | 41541 | 065E |  | 41631 |
| PF A | 0552 |  | 41363 | 05AC |  | 41453 | 0606 |  | 41543 | 0660 |  | 41633 |
| PF B | 0554 |  | 41365 | 05AE |  | 41455 | 0608 |  | 41545 | 0662 |  | 41635 |
| PF C | 0556 |  | 41367 | 05B0 |  | 41457 | 060A |  | 41547 | 0664 |  | 41637 |

See next page for continuation and description.

|  | INST (D) | AVE (A) | MAX (X) | MIN (I) |
| --- | --- | --- | --- | --- |
| THD VOLT A | 0558 |  | 41369 | 05B2 |  | 41459 | 060C |  | 41548 | 0666 |  | 41639 |
| THD VOLT B | 055A |  | 41371 | 05B4 |  | 41461 | 060E |  | 41551 | 0668 |  | 41641 |
| THD VOLT C | 055C |  | 41373 | 05B6 |  | 41463 | 0610 |  | 41553 | 066A |  | 41643 |
| THD AMP A | 055E |  | 41375 | 05B8 |  | 41465 | 0612 |  | 41555 | 066C |  | 41645 |
| THD AMP B | 0560 |  | 41377 | 05BA |  | 41467 | 0614 |  | 41557 | 066E |  | 41647 |
| THD AMP C | 0562 |  | 41379 | 05BC |  | 41469 | 0616 |  | 41559 | 0670 |  | 41649 |
| KF VOLT A | 0564 |  | 41381 | 05BE |  | 41471 | 0618 |  | 41561 | 0672 |  | 41651 |
| KF VOLT B | 0566 |  | 41383 | 05C0 |  | 41473 | 061A |  | 41563 | 0674 |  | 41653 |
| KF VOLT C | 0568 |  | 41385 | 05C2 |  | 41475 | 061C |  | 41565 | 0676 |  | 41655 |
| KF AMP A | 056A |  | 41387 | 05C4 |  | 41477 | 061E |  | 41567 | 0678 |  | 41657 |
| KF AMP B | 056C |  | 41389 | 05C6 |  | 41479 | 0620 |  | 41569 | 067A |  | 41659 |
| KF AMP C | 056E |  | 41391 | 05C8 |  | 41481 | 0622 |  | 41571 | 067C |  | 41661 |
| RESERVED | 0570 |  | 41393 | 05CA |  | 41483 | 0624 |  | 41573 | 067E |  | 41663 |
| RESERVED | 0572 |  | 41395 | 05CC |  | 41485 | 0626 |  | 41575 | 0680 |  | 41665 |
| RESERVED | 0574 |  | 41397 | 05CF |  | 41487 | 0628 |  | 41577 | 0682 |  | 41667 |
| RESERVED | 0576 |  | 41399 | 05D0 |  | 41489 | 062A |  | 41579 | 0684 |  | 41669 |
| RESERVED | 0578 |  | 41401 | 05D2 |  | 41491 | 062C |  | 41581 | 0686 |  | 41671 |
| RESERVED | 057A |  | 41403 | 05D4 |  | 41493 | 062E |  | 41583 | 0688 |  | 41673 |

Registers 0522-0689:

Every 2 registers hold a 4 byte floating-point number.  The format of a pair of registers is as follows:

| Registers |  |  |  |  |  |  |  |  |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | REGISTER 0 | REGISTER 1 |  |
|  | 15 | 14 |  | 7 | 6 |  | 0 | 15 |  | 0 |  |
|  | Sign | Exponent | Fraction |  |
| 0522+ | 0 | 7 |  | 0 | 22 |  |  |  |  | 0 | 41315+ |

FLOATING-POINT NEGATIVE MAX/MIN BLOCK

|  | Registers |  | 584/984 | Registers |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- |
|  | NEG MAX |  |  | NEG MIN |  |  |
| WATT | 068A |  | 41675 | 06A2 |  | 41699 |
| VAR | 068C |  | 41677 | 06A4 |  | 41701 |
| PF | 068E |  | 41679 | 06A6 |  | 41703 |
| WATT A | 0690 |  | 41681 | 06A8 |  | 41705 |
| WATT B | 0692 |  | 41683 | 06AA |  | 41707 |
| WATT C | 0694 |  | 41685 | 06AC |  | 41709 |
| VAR A | 0696 |  | 41687 | 06AE |  | 41711 |
| VAR B | 0698 |  | 41689 | 06B0 |  | 41713 |
| VAR C | 069A |  | 41691 | 06B2 |  | 41715 |
| PF A | 069C |  | 41693 | 06B4 |  | 41717 |
| PF B | 069E |  | 41695 | 06B6 |  | 41719 |
| PF C | 06A0 |  | 41697 | 06B8 |  | 41721 |

Registers 068A-06B9:

Every 2 registers hold a 4-byte floating-point number.

FLOATING-POINT THD DETAIL BLOCK

HARM VOLT A Registers

|  |  | Registers |  |  | 584/984 | Registers |  |  | 584/984 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | PERCENT |  |  |  | PHASE |  |  |  |
|  | HARM 0 | 06BA |  |  | 41723 | 06BC |  |  | 41725 |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 0736 |  |  | 41847 | 0738 |  |  | 41849 |

HARM VOLT B Registers

|  | HARM 0 | 073A |  |  | 41851 | 073C |  |  | 41853 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 07B6 |  |  | 41975 | 07B8 |  |  | 41977 |

HARM VOLT C Registers

|  | HARM 0 | 07BA |  |  | 41979 | 0303 |  |  | 41981 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 0836 |  |  | 42103 | 0838 |  |  | 41205 |

HARM AMP A Registers

|  | HARM 0 | 083A |  |  | 42107 | 083C |  |  | 42109 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 08B6 |  |  | 42231 | 08B8 |  |  | 42233 |

HARM AMP B Registers

|  | HARM 0 | 08BA |  |  | 42235 | 08BC |  |  | 42237 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 0936 |  |  | 42359 | 0938 |  |  | 42361 |

HARM AMP C Registers

|  | HARM 0 | 093A |  |  | 42363 | 093C |  |  | 42365 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ¦ | ¦ |  |  | ¦ | ¦ |  |  | ¦ |
|  | HARM 31 | 09B6 |  |  | 42487 | 09B8 |  |  | 42489 |

Register 0202-04C1:

Negative Hour Block

Registers									     584/984

0	1	2	3	4	5	6	7

-WATT HOUR

09BA +								      42491+

-VAR HOUR

09C2+								      42499+

For Description : see description for HOUR BLOCK on page 5.

Appendix D: Mass Memory & Null Terminated Hour Readings

MASS MEMORY COUNTER

Registers 09CA-09CD:

4-byte or 2-byte 2’s compliment numbers representing the number of Snapshots, Events or Waveforms stored in the mass   memory of the meter.

Null-Terminated Hour Readings

Registers                                                                                                                                                                       	         584/984

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- | --- |

WATT HOUR

| 09CE+ |  |  |  |  |  |  |  |  | 42511+ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

VAR HOUR

| 09D6+ |  |  |  |  |  |  |  |  | 42519+ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

VA HOUR

| 09DE+ |  |  |  |  |  |  |  |  | 42527+ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

-WATT HOUR

| 09E6+ |  |  |  |  |  |  |  |  | 42535+ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

-VAR HOUR

| 09EE+ |  |  |  |  |  |  |  |  | 42543+ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Registers 09CE-09F5:

16 Bytes each ASCII, representing a 15 Byte BCD count of the Hour Function.  The least significant byte of the last register in each Hour Reading is the ASCII null character ( 0x 00 ).

________________________________________________________________________________________________________________________________________

EXCEPTION FLAGS

|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 09F6 | L1 | L2 | R | I | W | - | - | - | - | - | - | - | - | - | - | - | 42551 |

Register 09F6:

L1 :	A bit value of 1 means a Limit 1 is exceeded. Cleared when Read.

A bit value of 0 means no Limit 1’s are exceeded.

L2: 	A bit value of 1 means a Limit 2 is exceeded. Cleared when Read.

A bit value of 0 means no Limit 2’s are exceeded.

R: 	A bit value of 1 means a Relay is energized. Cleared when Read.

A bit value of 0 means no Relays are energized.

I: 	A bit value of 1 means an Input is active.

A bit value of 0 means no Inputs are active.

W: 	A bit value of 1 means at least 1 Waveform is stored.

A bit value of 0 means no Waveforms are stored.

Input Status:

|  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 09f7 | I1 | I2 | I3 | I4 | - | - | - | - | - | - | - | - | - | - | - | - | 42552 |

Register 09F7:

A bit value of 1 means the associated input is active

A bit value of 0 means the associated input is not active.