Generic Specification For ProtoCom/ProtoCom-Lon Add-on Protocol Gateway

2.    	PRODUCT

2.1  	Protocol Gateway

- The unit shall be CE marked.

- The unit shall be a standalone device that can connect to Electro Industries (EIG)’s meters, and GE’s PQMII meter, through the meters’ RS485 serial port.

- The unit shall take the Modbus protocol data from the meter and translate it into other protocols.

  - The unit shall be available in two models.

  - 1 model shall take the Modbus protocol data and change it into BACnet/IP, BACnet MS/TP, DF1, EtherNet/IP, or Metasys N2 protocol

  - 1 model shall take the Modbus protocol data and change it into LonWorks protocol.

D.	The unit shall have appropriate serial port and Ethernet connections to connect to the field protocol Host unit.

- The unit shall have the capability to automatically detect which EIG meter it is connected to.

  - The unit shall load into memory all object lists for the available protocols for the meter as soon as the meter is auto-detected.

  - Auto-discovery shall be enabled and disabled via Dip switches.

- The unit support the following EIG meters:

  - Shark® 100 meter

  - Shark® 200 meter

  - Shark® 270 meter

  - Nexus® 1252 meter

  - Nexus® 1262 meter

  - Nexus® 1272 meter

  - Nexus® 1500 meter

  - MP200-Y metering system

  - MP200-S metering system

  - DMMS 425 meter

  - PQMII meter

- The unit shall supply up to 1500 BACnet data points and up to 1000 LonWorks data points; supporting multiple meters The number of power and energy data points supplied for each of the EIG meters is as follows:

  - Shark® 100 meter: 56

  - Shark® 200 meter: 68

  - Shark® 270 meter: 67

  - Nexus® 1252 meter: 48

  - Nexus® 1262 meter: 48

  - Nexus® 1272 meter: 48

  - Nexus® 1500 meter: 56

  - MP200-Y metering system: 241

  - MP200-S metering system: 571

  - DMMS 425 meter: 46

  - PQMII meter: 62

- DIP switches shall be used to set MAC Address, Node-ID, and Baud Rate for the unit.

- The unit shall have a graphical user interface (GUI).

  - The GUI shall be viewable through any standard Web browser.

  - The GUI shall provide the capability of changing the device’s IP address for use with BACnet/IP and EtherNet/IP protocols.

  - The GUI shall provide the capability of changing the Node Offset for use with BACnet/IP and BACnet MS/TP protocols.

  - The GUI shall contain EIG contact information.

- The unit shall have a password protection option.

- The unit’s RS485 connection shall be a 6-pin input supporting both RS485 communication and 9-30 VDC/12-24VAC power supply.

- The unit shall come in a kit that includes the unit, a 3 foot RS485 communication cable, a 120/220V to 24VDC power supply, a user manual on a CD, and a Quickstart guide.

- The unit’s dimensions shall be: 4.5 L x 3.2 W x 1.6 in H (11.5 cm L x 8.3 cm W x 4.1 cm H).

- The unit’s operating temperature shall be: ‐40°F to167°F (‐40°C to 75°C).

- The unit shall have a standard 4-year warranty.

P.  The following models shall be acceptable:

a. ProtoCom-KT - ProtoCom Kit for BACnet and other protocols provided by Electro Industries / GaugeTech, Westbury NY 516-334-0870 www.electroind.com

b. ProtoCom-Lon-KT - ProtoCom-Lon Kit for LonWorks protocol provided by Electro Industries / GaugeTech 516-334-0870 www.electroind.com

- For specification questions, contact:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741

www.electroind.com