Generic Specification For

Multifunction Power and energy meter

## Shark ® 100 meter  in Enclosure

2.    	PRODUCT

2.1  	POWER METERS

- The meter shall be UL listed and CE marked.

B.	The meter shall come pre-wired as per NEC coloring code in either a UL approved NEMA 1 enclosure or a UL approved NEMA 4X enclosure.

1. 	The enclosure shall be available in four configurations:

  - (120-240) V AC line powered.

  - 277/480 V AC line powered - comes equipped with a control power transformer.

  - (18-60) V DC external powered.

  - Universal, (120-240) V AC @ 50/60 Hz or (100-370) V DC external powered.

2.    The enclosure shall come with voltage fuses and a shorting block for use with 
        current transformers.

3.	The enclosure shall have a lockable door.

C.  The meter shall be designed for Multifunction Electrical Measurement on 3 phase power systems. The meter shall perform to spec in harsh electrical applications in high and low voltage power systems.

- The meter shall support 3-Element Wye, 2.5 Element Wye, 2 Element Delta, 4 wire Delta systems.

- The meter shall accept universal voltage input.

- The meter's surge withstand shall conform to IEEE C37.90.1.

- The meter shall be user programmable for voltage range to any PT ratio.

- The meter shall accept a burden up to 0.36 VA per phase, Max at 600 V, and 0.014 VA at 120 V.

- The meter shall accept a voltage input range of up to 416 volts Line to Neutral and up to 721 volts Line to Line.

- The meter shall accept a current reading of up to 11 A continuous.

- The meter shall have color-coordinated voltage and current inputs.

- The meter shall have a phasor diagram that clearly shows wiring status.

D.	  The meter shall use a dual input method for current inputs.  Method one shall allow the
       CT to pass directly through the meter without any physical termination on the meter. 
       The second method shall provide additional termination pass-through bars, allowing the 
       CT leads to be terminated on the meter.  The meter must support both termination 
        methods.

    - Fault Current Withstand shall be 100 A for 10 seconds, 300 A for 3 seconds, and 500 A for 1 second.

    - The meter shall be programmable for current to any CT ratio.

    - The meter shall accept a burden of 0.005 VA per phase Max at 11 A.

    - The meter shall begin reading at 0.1% of the nominal current.

    - Pass through wire gauge dimension of 0.177” / 4.5 mm shall be available.

    - All inputs and outputs shall be galvanically isolated to 2500 volts AC.

    - The meter shall accept current inputs of class 10: (0 to 10) A, 5 A Nominal, and class 2 (0 to 2) A, 1 A Nominal Secondary.

E.	The meter shall have an accuracy of +/- 0.1% or better for voltage and current, and 0.2% for power and energy functions.  The meter shall have a Frequency measurement accuracy +/- 0.01Hz or better. The meter shall meet the accuracy requirements of IEC 62053-22 (0.2S Class) and ANSI C12.20 (0.2 Accuracy Class).

- The meter shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral.

- The meter shall provide sampling at 400+ samples per cycle on all channels measured readings simultaneously.

- The meter shall utilize 24 bit Analog to Digital conversion.

- The meter shall provide THD (% of Total Harmonic Distortion).

F.	The meter shall include a three-line, bright red, .56” LED display.

1.   The meter must display a % of Load Bar on the front panel to provide an analog 
            feel.  The % Load bar shall have not less than 10 segments.

G.	The meter shall be a traceable revenue meter, which shall contain a utility grade test 
      pulse allowing power providers to verify and confirm that the meter is performing to its
      rated accuracy.

H.   The meter shall include virtual measurement upgrade packs (V-Switch™ keys), which
       shall allow user to upgrade in field without removing installed meter.

- Four upgrade packs shall be:

  - Volts and A Meter – Default

  - Volts, A, kW, kVAR, PF, kVA, Freq.

  - Volts, A, kW, kVAR, PF, kVA, Freq., kWh, kVAh, kVARh.

  - Volts, A, kW, kVAR, PF, kVA, Freq., kWh, kVAh, kVARh, THD Monitoring and Limit Exceeded Alarms.

2.   The V-Switch™ keys must be able to be updated without physically removing the installed meter.

3.   The meter shall be a traceable revenue meter, which shall contain a utility grade
      test pulse allowing power providers to verify and confirm that the meter is 
      performing to its rated accuracy.

I.	The meter shall include 2 independent communications ports on the back and face plate, with advanced features.

- One port shall provide RS485 communication speaking Modbus ASCII, Modbus RTU, or DNP3 protocol through back plate.

- Baud rates shall be from 9,600 baud to 57,600 baud.

- The meter shall provide an optical IrDA port (through faceplate), as the second communication port, which shall allow the unit to be set up and programmed using a remote laptop PC without need for a communication cable.

- Meter shall have 8 Bit, No parity.

J.	The meter shall have optional 100BaseT Ethernet communication capability.

1. Ethernet communication shall consist of Modbus protocol over TCP/IP.

K.  The meter shall provide user configured fixed window or rolling window demand.  This shall allow user to set up the particular utility demand profile.

- Readings for kW, kVAR, kVA and PF shall be calculated using utility demand features.

- All other parameters shall offer max and min capability over the user selectable averaging period.

- Voltage shall provide an instantaneous max and min reading displaying the highest surge and lowest sag seen by the meter.

L.	  Meter shall provide update rate of every 6 cycles for Watts, VAR, and VA.  All other 
        parameters shall be every 60 cycles.

M.   The meter shall have a standard 4-year warranty.

N.   Power meter shall be able to be stored in (-20 to +70) degrees C.

- Operating temperature shall be (-20 to +70) degrees C.

O.  The following options shall be available for ordering:

| Model | Voltage | Frequency | Current Class | V-Switch Pack | Power Supply | Communication Format (Shark 100 Only) |
| --- | --- | --- | --- | --- | --- | --- |
| ENCSHK100 Shark® 100 Meter in NEMA 1 Enclosure ENC4XSHK100 Shark® 100 Meter in NEMA 4X Enclosure | -120: (120-240) V AC Line Powered -277: 277/480 V AC Line Powered -EXT24* (18-60) V DC External Powered -EXT120 (120-240) V AC @ 50/60 Hz or (100-370) V DC External Powered | -50: 50 HZ System -60: 60 HZ System | -10: 5 A Secondary -2 : 1 A Secondary | -V1: Default V-Switch Volts/Amps -V2: Above with Power and Freq. -V3: Above plus DNP3 and Energy Counters -V4: Above with Harmonics and Limits | -D2 (120-240) V AC @ 50/60 Hz or (100-370) V DC -D* (18-60) V DC | -X: No Com -485P: RS485 -INP10: 100BaseT Ethernet |

* These two options must be ordered together.

P.	  Example product is Electro Industries/GaugeTech, 
       Model ENC4XSHK100-120-60-10-V1-485P for 120 V AC power systems

- Add the following suffixes for added options:

a.	(9PINC) – RS232 Cable

b.	(Unicom 2500) – RS485 to RS232 Converter

c.	(Unicom 2500-F) – RS485 to RS232 to Fiber Optic Converter

d.	(Modem Manager, Model #, MM1) – RS485 to RS232 Converter for Modem Communication

  - (CAB6490) – IrDA to USB Adapter for Remote Read

f.	(Certificate of Calibration, Part #, CCal) – This provides Certificate of Calibration with NIST traceable test data.

g. 	(CT200K) – 200/5 Ratio, 1” Window 3 CTs

  - (CT400K) – 400/5 Ratio, 1.25” Window, 3 CTs

    - (CT800K) – 800/5 Ratio, 2.06” Window, 3 CTs

j.	(CT2000K) – 2000/5 Ratio, 3.00” Window, 3 CTs

    - (COMPQA6) – CommunicatorPQA® 6.0 Software Application

- For specification information, contact:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741

www.electroind.com

sales@electroind.com