Generic Specification For

Multifunction Power and energy meter

## Shark ® 50B meter in Enclosure

2.    	PRODUCT

2.1  	POWER METER

- The meter shall be UL listed and CE marked.

B.	The meter shall come pre-wired as per NEC coloring code in either a UL approved NEMA 1 enclosure or a UL approved NEMA 4X enclosure.

1. 	The enclosure shall be available in three configurations:

  - (120-240) V AC line powered.

  - 277/480 V AC line powered - comes equipped with a control power transformer.

  - Universal, (120-240) V AC @ 50/60 Hz or (100-370) V DC external powered.

2.    The enclosure shall come with Voltage fuses and a shorting block for use with 
        current transformers.

3.	The enclosure shall have a lockable door.

C.	The meter shall be designed for Multifunction Electrical Measurement on 3 phase power systems. The meter shall perform to spec in harsh electrical applications in high and low voltage power systems.

- The meter shall support 3-Element Wye, 2.5 Element Wye, 2 Element Delta, 4 wire Delta systems.

- The meter shall accept universal voltage input.

- The meter's surge withstand shall conform to IEEE C37.90.1.

- The meter shall be user programmable for voltage range to any PT ratio.

- The meter shall accept a burden up to 0.36VA per phase, Max at 600V, and 0.014VA at 120 Volts.

- The meter shall accept a voltage input range of up to 416 Volts Line to Neutral, and up to 721 Volts Line to Line.

- The meter shall accept a current reading of up to 11 Amps continuous.

- The meter shall have color-coordinated voltage and current inputs.

- The meter shall have a phasor diagram that clearly shows wiring status.

D.	 The meter shall use a dual input method for current inputs.  Method one shall allow the 
      CT to pass directly through the meter without any physical termination on the meter.
      The second method shall provide additional termination pass-through bars, allowing the 
      CT leads to be terminated on the meter.  The meter must support both termination 
      methods.

    - Fault Current Withstand shall be 100 Amps for 10 seconds, 300 Amps for 3 seconds, and 500 Amps for 1 second.

    - The meter shall be programmable for current to any CT ratio.  The meter shall accept a burden of 0.005VA per phase, Max at 11 Amps.

    - The meter shall begin reading at 0.1% of nominal current.

    - Pass through wire gauge dimension of 0.177” / 4.5 mm shall be available.

    - All inputs and outputs shall be galvanically isolated to 2500 Volts AC.

    - The meter shall accept current inputs of class 10: (0 to 10) A, 5 Amp Nominal, and class 2 (0 to 2) A, 1A Nominal Secondary.

E.	The meter shall have an accuracy of +/- 0.4% or better for Volts and Amps, and 0.5% for power and energy functions.  The meter shall have Frequency measurement accuracy +/- 0.01Hz or better. The meter shall meet the accuracy requirements of IEC 62053-22 (Class 0.5%) and ANSI C12.20 (Class 0.5%).

- The meter shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral.

- The meter shall provide sampling at 400+ samples per cycle on all channels measured readings simultaneously.

- The meter shall have 6 simultaneous 24-bit Analog to Digital converters.

- The meter shall have an anti-dither algorithm to improve reading stability.

F.	The meter shall have a three line, bright red, .56” LED display, which presents a scrolling display of measured readings.

- The meter shall display a % of Load bar on the front panel to provide an analog feel. The % of Load bar shall have not less than 10 segments.

G.	The meter shall have an RS485 Com port through its back plate, which shall 
       communicate native BACnet MS/TP protocol for full integration into Building 
      Management Systems that use BACnet protocol.

- The meter’s BACnet MS/TP shall have 34 pre-programmed BACnet Objects 
      consisting of standard voltage, current, and power parameters. The Objects shall 
      be named such that they can be readily identified.

- No programming shall be necessary to use the meter’s BACnet MS/TP.

H. 	The meter shall have an RJ45 10/100BaseT Ethernet Com port through its back plate, 
      which shall communicate Modbus TCP/IP.

- The Ethernet port shall enable optional BACnet MS/TP configuration through embedded webpages.

- The Ethernet port shall provide a Web server for viewing meter readings through the Internet.

- The Web server shall support standard Web browsers.

I.  The meter shall provide user configured fixed window or rolling window demand so the 
     user can set up the particular utility demand profile.

- Readings for kW, kVAR, kVA and PF shall be calculated using utility demand features. All other parameters shall offer max and min capability over the user selectable averaging period.

- Voltage shall provide an instantaneous max and min reading displaying the highest surge and lowest sag seen by the meter.

J.   The meter shall have a 4-year warranty.

K. 	The following options shall be available for ordering:

| Model | Voltage |
| --- | --- |
| ENCSHK50B Shark® 50B meter in NEMA 1 Enclosure ENC4XSHK50B Shark® 50B meter in NEMA 4X Enclosure | -120: (120-240) V AC Line Powered |
|  | -277: 277/480 V AC Line Powered |
|  | -EXT120 (120-240) V AC @50/60 Hz or (100-370) V DC External Powered |

L. For specification information, contact:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741

www.electroind.com

sales@electroind.com