Generic Specification For

Multifunction Power and energy meter

## Shark ® 100B/BT meter

2.    	PRODUCT

2.1  	POWER METERS

- The meter shall be UL listed and CE marked.

B.	The meter shall be designed for Multifunction Electrical Measurement on 3 phase power systems. The meter shall perform to spec in harsh electrical applications in high and low voltage power systems.

- The meter shall support 3-Element Wye, 2.5 Element Wye, 2 Element Delta, 4 wire Delta systems.

- The meter shall accept universal voltage input.

- The meter's surge withstand shall conform to IEEE C37.90.1.

- The meter shall be user programmable for voltage range to any PT ratio.

- The meter shall accept a burden up to 0.36VA per phase, Max at 600V, and 0.014VA at 120 Volts.

- The meter shall accept a voltage input range of up to 416 Volts Line to Neutral, and  up to 721 Volts Line to Line.

- The meter shall accept a current reading of up to 11 Amps continuous.

- The meter shall have color-coordinated voltage and current inputs.

- The meter shall have a phasor diagram that clearly shows wiring status.

- Power meter shall use a dual input method for current inputs.  Method one shall allow the CT to pass directly through the meter without any physical termination on the meter, ensuring the meter cannot be a point of failure on the CT circuit.  The second method shall provide additional termination pass-through bars, allowing the CT leads to be terminated on the meter.  The meter must support both termination methods.

    - Fault Current Withstand shall be 100 Amps for 10 seconds, 300 Amps for 3 seconds, and 500 Amps for 1 second.

    - Meter shall be programmable for current to any CT ratio.  DIP switches or other fixed ratios shall not be acceptable

    - Meter shall accept burden of 0.005VA per phase, Max at 11 Amps.

    - Meter shall begin reading at a 5mA pickup current.

    - Pass through wire gauge dimension of 0.177” / 4.5 mm shall be available.

    - All inputs and outputs shall be galvanically isolated to 2500 Volts AC.

    - The meter shall accept current inputs of class 10: (0 to 11) A, 5 Amp Nominal, and class 2 (0 to 2) A, 1A Nominal Secondary.

D.	The meter shall have an accuracy of +/- 0.1% or better for volts and amps, and 0.2% for power and energy functions.  The meter shall meet the accuracy requirements of IEC62053-22 (Class 0.2%) and ANSI C12.201(Class 0.2%).

- The meter shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral.

- The meter shall provide sampling at 400+ samples per cycle on all channels measured readings simultaneously.

- The meter shall utilize 24 bit Analog to Digital conversion.

- Meter shall provide Harmonics %THD (% of total Harmonic Distortion).

E.	The meter shall include a three line, bright red, .56” LED display.

- The meter shall fit in both DIN 92mm and ANSI C39.1 Round cut-outs.

- The meter must display a % of Load Bar on the front panel to provide an analog feel.  The % Load bar shall have not less than 10 segments.

  - Meter shall be available in transducer only version, which shall not include a display. The meter shall mount directly to a DIN rail.

- Meter shall be a traceable revenue meter, which shall contain a utility grade test pulse allowing power providers to verify and confirm that the meter is performing to its rated accuracy.

H.	The meter shall include 2 independent communications ports on the back and face plate, with advanced features.

- One port, through backplate, shall be an RJ45 port, providing 100BaseT Ethernet communication speaking BACnet/IP protocol and Modbus TCP, and a Web server.

- The meter shall provide an optical IrDA port (through faceplate), as the second communication port, which shall allow the unit to be set up and programmed using a remote laptop PC without need for a communication cable.

I.  The meter shall provide user configured fixed window or rolling window demand.  This shall allow user to set up the particular utility demand profile.

- Readings for kW, kVAR, kVA and PF shall be calculated using utility demand features.

- All other parameters shall offer max and min capability over the user selectable averaging period.

- Voltage shall provide an instantaneous max and min reading displaying the highest surge and lowest sag seen by the meter.

J.  The meter shall support power supply of 90 to 265 Volts AC and 100 to 370 Volts DC.  Universal AC/DC Supply shall be available.

- Meter power supply shall accept burden of 10VA max.

- Meter shall provide upgrade rate of 100msec for Watts, Var and VA.  All other parameters shall be 1 second.

K.  The meter shall have native BACnet/IP protocol.

1.   The meter shall provide 62 embedded BACnet Objects consisting of standard 
            voltage, current, and power parameters. The Objects shall be named such that 
            they can be readily identified.

2.   The meter shall have an embedded Web interface for configuration and viewing.

a.  The Web interface shall have a Home page with power and energy snapshot 
                  information.

b.  The Web interface shall have a page for configuring the BACnet/IP settings, 
                  including IP address, Network mask, Default Gateway, and the like.

c.  The Web interface shall allow the user to activate the new configuration and
                  reboot the meter.

d.  The Web interface shall have a feature that lets the user download BACnet 
	           Object data as a .csv file that can be viewed in MS Excel© or saved as an MS 
	           Excel© file.

e.  The Web interface shall have a webpage that displays the BACnet objects, 
	           their readings, and information about the objects.

f.  The Web interface shall have a webpage displaying statistics for the unit, e.g., 
	           the number of meter reboots, and the number of BACnet/IP packets sent and 
                 received.

g.  The Web interface shall allow the user to discard any changes and return to the 
	           saved configuration, or return to the factory default configuration.

h.   The Web interface shall be viewable with any standard Internet browser.

3.   The meter shall be configurable on the Host PC through LAN configuration.

4.   The meter’s BACnet/IP shall integrate with any BACnet applications or servers.

5.   The meter shall also have an open socket for Modbus TCP that shall be 
            simultaneously available through the LAN interface.

L.  The meter shall have a standard 4-year warranty.

M.  Power meter shall be able to be stored in (-20 to +70) degrees C.

- Operating temperature shall be (-20 to +70) degrees C.

- NEMA 12 faceplate rating shall be available for the power meter.

N.    The following options shall be available for ordering:

| Options | Model | Frequency | Current Class | Power Supply | Mounting (Shark 100 Only) |
| --- | --- | --- | --- | --- | --- |
|  | Shark100B: Meter/Transducer | -50: 50 HZ System | -10: 5 Amp Secondary | -D2 (90-265)VAC or (100-370)VDC | -X: ANSI Mounting |
|  | Shark100BT: Transducer Only | -60: 60 HZ System | -2 : 1 Amp Secondary | -D (18-60)VDC | -DIN: DIN Mounting Brackets |

O.    Acceptable product is Electro Industries/GaugeTech, SHARK100B-60-10-D2-X.

For specification information, contact:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741

www.electroind.com

sales@electroind.com