Generic Specification For

Electronic submeter with advanced wifi ethernet capability

## Shark 100-S

2.    	PRODUCT

2.1  	Wireless Submeter

A.	Submeter shall be designed for Multifunction Electrical Measurement on 3 phase power systems.

- Submeter shall support 3 element wye, 2.5 element wye, 2 element delta, 4 wire delta systems.

- The submeter shall accept universal voltage input suitable for 120, 220, and 277 power systems.

- Surge withstand shall conform to IEEE C37.90.1

- The submeter shall be user programmable for voltage range to any PT ratio.

- The submeter shall accept a voltage input range of up to 416 volts Line to Neutral, and a range of up to 721 volts Line to Line.

- Submeter shall accept a current reading of up to 11 A continuous.

B.	The submeter shall have an accuracy of +/- 0.1% or better for voltage and current, and 0.2% for power and energy functions.  The submeter shall meet the accuracy requirements of IEC 62053-22 (0.2S Class) and ANSI C12.20 (0.2 Accuracy Class).

- The submeter shall provide true RMS measurements of voltage, phase to neutral and phase to phase, current, per phase and neutral.

- The submeter shall provide sampling at 400+ samples per cycle on all channel measured readings simultaneously.

- The submeter shall utilize 24 bit Analog to Digital conversion.

- Submeter shall provide THD (% of total Harmonic Distortion).

C.	The submeter shall include a three line, bright red, .56” LED display.

- The submeter shall fit in both DIN 92 mm and ANSI C39.1 Round cut-outs.

- The submeter must display a % of Load Bar on the front panel to provide an analog feel.  The % Load bar shall have no less than 10 segments.

- The submeter must have a programmable display, which allows for the following programming functions including automatic scroll, screen selection programming, and energy scaling.

- Submeter shall include virtual measurement upgrade packs, which shall allow user to upgrade in field without removing installed submeter.

- Two upgrade packs shall be:

  - Volts, A, kW, kVAR, PF, kVA, Freq., kWh, kVAh, kVARh.

  - Volts, A, kW, kVAR, PF, kVA, Freq., kWh, kVAh, kVARh, THD Monitoring and Limit Exceeded Alarms.

- These virtual upgrade packs must be able to be updated without physically removing the installed submeter.

- Submeter shall be a traceable revenue submeter, which shall contain a utility grade test pulse, allowing power providers to verify and confirm that the submeter is performing to its rated accuracy.

E.	The submeter shall include two independent communication ports with advanced features.

- Port 1 shall provide an optical IrDA port (through the faceplate) which shall allow the unit to be set up and programmed using a PDA or remote laptop without need for a communication cable.

- Port 2 shall be selectable for RS485 communication, for 10BaseT Ethernet or for 802.11 Wireless Ethernet.

- When in serial mode, the meter shall speak Modbus ASCII, Modbus RTU, or DNP3 protocol up to 57.6K baud.

- When in Ethernet mode, the meter shall provide an 802.11 WIFI or an RJ45 Ethernet connection which shall allow the unit to be assigned an IP address and communicate Modbus protocol over Ethernet TCP/IP.

- The submeter shall have Pocket PC based software available for remote programming and integration.

F.  The submeter shall provide user configured fixed window or rolling window demand.  This shall allow user to set up the particular utility demand profile.

- Readings for kW, kVAR, kVA and PF shall be calculated using utility demand features.

- All other parameters shall offer max and min capability over the user selectable averaging period.

- Voltage shall provide an instantaneous max and min reading, displaying the highest surge and lowest sag seen by the submeter.

- The meter shall additionally measure accumulated energy in both generating and consuming quadrants with a programmable scaling that allow up to 8 digits of energy resolution.

- The meter shall also accumulate positive and negative VAR-hours and VA-hours. All readings shall be stamped with a positive and negative average demand.

G.  The submeter shall support power supply and support direct wiring from (100 to 400) volts AC or (100 to 370) volts DC.

- Submeter power supply shall accept burden of 10 VA max.

  - The submeter shall have a standard 4-year warranty.

I.   Submeter shall be able to be stored in (-40 to +85) degrees C.

- Operating temperature shall be (-30 to +70) degrees C.

- NEMA 12 faceplate rating shall be available for the Submeter.

J.  The following options shall be available for ordering:

|  | Model | Frequency | Current Class | V-Switch Pack | Communication Format |
| --- | --- | --- | --- | --- | --- |
|  | Shark 100-S | -50: 50 HZ System -60: 60 HZ System | -10: 5 A Secondary -2 : 1 A Secondary | -V3: Default with Energy Counters -V4: Above with Harmonics and Limits | -485: RS485 -WIFI: Wireless and LAN Based Ethernet |

K.	  Acceptable product is Electro Industries/GaugeTech, Model Shark 100-S.

- Add the following suffixes for added options:

a.	(CAB 6490) – USB to IrDA Adapter for Programming

b.	(Unicom 2500) – RS485 to RS232 Converter

c.	(Unicom 2500-F) – RS485 to RS232 to Fiber Optic Converter

d.	(Modem Manager, Model #, MM1) – RS485 to RS232 Converter for    Modem Communication

e.	(Certificate of Calibration, Part #, CCal) – This provides Certificate of Calibration with NIST traceable test data.

f. 	(CT200K) – 200/5 Ratio, .94” Window 3 CTs

      - (CT400K) – 400/5 Ratio, 1.25” Window, 3 CTs

h.         (CT800K) – 800/5 Ratio, 2.06” Window, 3 CTs

i.          (CT2000K) – 2000/5 Ratio, 3.00” Window, 3 CTs

    - (COMPQA5) – CommunicatorPQA™ 5.0 Software Application

- For specification information, contact:

Electro Industries/GaugeTech

1800 Shames Drive

Westbury, NY 11590

Phone: 516-334-0870

Fax: 516-338-4741